SITE ACCEPTANCE REPORT

- SITE INFORMATION

| Project No |  | System Size Installed |  |
| --- | --- | --- | --- |
| Installation Start Date |  | Installation End Date |  |
| System Installer |  |  |  |
| PIC Onsite |  |  |  |
| Premise Adress |  |  |  |

Note:

Please ensure that the information filled out is correct.

2.0 SYSTEM COMPONENTS INSTALLED

| Item | Description | Quantity/Length |
| --- | --- | --- |
| PV Solar Panels | [Brand, Model & Serial Num] – for each Solar Panels |  |
| Inverter | [Brand & Model & Serial Num] |  |
| Wifi Dongle (for 3 phase string inverter) | [Brand & Model & Serial Num] |  |
| Mounting Structure | [Brand & Model] |  |
| DC Cabling | [Brand & Model] |  |
| AC Cabling | [Brand & Model] |  |
| Earth Cabling | [Brand & Model] |  |
| Junction Box (for Micro Inverter System) | [Brand & Model] |  |
| Solar combiner box | [Brand & Model] |  |
| AC breakers | [Brand & Model] |  |
| AC SPD | [Brand & Model] |  |
| RCCB (for Micro Inverter System) | [Brand & Model] |  |
| Energy Meter | [Brand & Model] |  |
| Smart Meter | [Brand & Model] |  |

3.0 DRAWINGS (SLD and PV drawings shall be stamped by SEDA certified personnel)

- Single Line Diagram

- PV Layout submission to SEDA

4.0 INSTALLATION PHOTOGRAPHS

Notes:

*Photos to be captured with GPS (latitude / longitude) information, time and date shown

*Please attach maximum 3 photographs per page, please ensure that photographs are of great viewing quality.

* All photos must be labelled accordingly

- Installation Mount Photos

1.Mounting Hooks and brackets (Hook bracket/L-feet)

2.Photo of entire mounting layout

- Solar Panel Array Layout

- AC and DC Cable Route

- Cable from PV array to Drop point (Cables on roof level)

- Vertical Cable route (from drop point to inverter/combiner box)

- Junction Box – (for microinverter only)

- Combiner box to Premise DB

- Inverter/Combiner box

- Zoom out view of Inverter with Combiner Box

- Close up view of Inverter (applicable for String Inverter only)

- AC output cables from String Inverter (Showing cable ferrule installed)

- Microinverters- (for microinverter system only)

- Combiner Box

- With cover on – (clear view of the labels of each component)

- Without cover – clear view of components ratings, terminations, color coded AC wires.

- Interconnection Point at the Customer’s Distribution Board (DB)

- Wide-angle view – clear view of the whole customer`s DB box.

- Zoomed picture of the breaker with Solar termination point)- Solar cable labelled Distinctive labe).

- Smart Meter (only for site with Smart meter)

- Power and communication lines checklist Connection Type; Wire; Smart Meter Terminals; Source; CAT6; Tick; Remark. Voltage Inputs; Ua(Red); 3; Load - R phase. Ub(Yellow); 6; Load - Y phase. Uc(Blue); 9; Load - Blue phase. Un(Neutral); 10; Load - Neutral. Current Transformer; IA*; 13; CT Y; White-Orange. IA; 14; CT Y; Orange. IB*; 16; CT B; White-Green. IB; 17; CT B; Green. IC*; 19; CT R; White-Blue. IC; 21; CT R; Blue. Communication; RS485A; 24; Smart Meter. RS485B; 25; Smart Meter.

- CT clamps pic showing direction of current flow arrow

- CT clamp connection to CAT 6 cable

- Connection Smart Meter terminals (input and output)

- Housekeeping at customer premise after installation completed.

- TESTING & COMISSIONING RESULTS

* Each test shall be supported with photos of testing gears (PV tester, Multimeter, Earth resistance tester) clearly showing the results and tally with the tabulated value.

* Each photos must be labelled accordingly.

5.1 Cable Insulation Test

| Cable Insulation Test |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Test Point |  | All cables |  |  |  |  |
| Use appropriate tools to measure and record |  |  |  |  |  |  |
| Testing is conducted on new cable installations to determine if the insulation has been damaged. Notes: Mandatory for all test on-site photographs to be attached and labelled accordingly. |  |  |  | Instructions: SWITCH OFF / DISCONNECT the following: - PV AC MCB Isolate all cables except for inter-module connection and earthing cables. |  |  |
| No. | Cable from (Originating) | Cable to (Terminating) | Insulation Resistance Value (M Ohms) |  | Pass | Fail |
|  |  |  |  |  | (Please tick the relevant box) |  |
| For String Inverter System |  |  |  |  |  |  |
| 1 | PV String 1 (+) | MPPT Inverter |  |  |  |  |
| 2 | PV String 1 (-) | MPPT Inverter |  |  |  |  |
| 3 | PV String 2 (+) | MPPT Inverter |  |  |  |  |
| 4 | PV String 2 (-) | MPPT Inverter |  |  |  |  |
| 5 | Inverter | AC MCB |  |  |  |  |
| 6 | AC MCB | PV Meter |  |  |  |  |
| 7 | AC MCB | AC SPD |  |  |  |  |
| 8 | PV Meter | Load Main Breaker |  |  |  |  |
| For Micro Inverter System |  |  |  |  |  |  |
| 1 | PV Panels | Microinverter 1 |  |  |  |  |
| 2 | PV Panels | Microinverter 2 |  |  |  |  |
| 3 | PV Panels | Microinverter 3 |  |  |  |  |
| 4 | PV Panels | Microinverter 4 |  |  |  |  |
| 5 | PV Panels | Microinverter 5 |  |  |  |  |
| 6 | PV Panels | Microinverter 6 |  |  |  |  |
| 7 | PV Panels | Microinverter 7 |  |  |  |  |
| 8 | Junction Box | AC MCB |  |  |  |  |
| 9 | AC MCB | ELCB/RCCB |  |  |  |  |
| 10 | ELCB/RCCB | PV Meter |  |  |  |  |
| 11 | AC MCB | AC SPD |  |  |  |  |
| 12k | PV Meter | Load Main Breaker |  |  |  |  |
| Photographs: SAMPLE SAMPLE Test 2.1.2 Test 2.1.1 |  |  |  |  |  |  |

  - String Open Circuit Voltage Test( Only for String Inverter )

| String Open Circuit Voltage Test |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Point |  | Solar Combiner Box |  |  |  |  |  |  |  |
| Use appropriate tools to measure and record |  |  |  |  |  |  |  |  |  |
| Test the continuity of each string |  |  |  |  |  | OK: |  | Not OK: |  |
| Determine the following: 1. Measured Open Circuit Voltage (Voc_mea) of each string. 2. Expected Open Circuit Voltage (Voc_exp) of each string. 3. % Difference between measured and expected Voc. ACCEPT if - % difference of Voc (between measured Voc and expected Voc) with respect to expected Voc is within +/- 5% - Voc measured of each string is less than the maximum input voltage of the inverter - Polarity of all DC cables (string and array) is correct Notes: Mandatory for all test on-site photographs to be attached and labelled accordingly. |  |  |  |  |  | Solar irradiance should be at least 350 Wm-2 when performing this test. Instructions: SWITCH OFF / DISCONNECT the following: - PV AC MCB |  |  |  |
| String No. | Voc of string at STC (V) |  | Voc measured (V) | Voc expected (V) | Measured module temp (oC) | Measured Irradiance (Wm-2) | % difference of Voc |  | Accept (A) or Reject (R) |
| 1 |  |  |  |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |  |  |
| Photographs: |  |  |  |  |  |  |  |  |  |

  - DC Short Circuit Current Test ( Only for String Inverter )

| DC Short Circuit Current Test |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Test Point | Solar Combiner Box |  |  |  |  |  |  |
| Use appropriate tools to measure and record |  |  |  |  |  |  |  |
| Using appropriate method, determine the following: 1. Measured short circuit current (Isc_mea) of each string 2. Expected short circuit current (Isc_exp) of each string 3. % Difference between measured and expected Isc. ACCEPT if % difference of Isc (between measured Isc_mea and expected Isc_exp) with respect to Isc_exp is within +/- 5% Notes: Mandatory for all test on-site photographs to be attached and labelled accordingly. |  |  |  |  | Solar irradiance should be at least 350 Wm-2 when performing this test. Instructions: SWITCH OFF / DISCONNECT the following: - PV AC MCB |  |  |
| No. String No. | Solar irradianc (Wm-2) | Measured module temp (oC) | Measured Isc of string (A) | Expected Isc of String (A) |  | % difference of Isc | Accept (A) or Reject (R) |
| Photographs: |  |  |  |  |  |  |  |

  - Isolation Device Functional Test

| Isolation Device Functional Test |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Test Point |  | All breakers and switches |  |  |  |
| Use appropriate tools to measure and record |  |  |  |  |  |
| Please tick in the appropriate box Notes: Mandatory for all test on-site photographs to be attached and labelled accordingly |  | Solar irradiance should be at least 350 Wm-2 when performing this test. Instructions: SWITCH OFF / DISCONNECT the following: - PV AC MCB |  |  |  |
| No. | Description |  | Accept | Reject | Note |
| 1 | Confirm voltage is NOT present at the outgoing terminal of PV AC MCB when the switch is in OFF position |  |  |  |  |
| 2 | Confirm voltage is present at the outgoing terminal of PV AC MCB when the switch is in ON position |  |  |  |  |
| Photographs: |  |  |  |  |  |

  - Inverter Functional Test and Incoming power supply measurement.

| Inverter Functional Test |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Point |  |  |  | Inverter |  |  |  |  |
| Use appropriate tools to measure and record |  |  |  |  |  |  |  |  |
| Notes: Mandatory for all test on-site photographs to be attached and labelled accordingly |  |  | Please tick in the appropriate box Solar irradiance should be at least 350 Wm-2 when performing this test. Instructions: SWITCH ON the system and ensure that the inverter is operating. CAUTION: Before switching on the inverter, make sure Voc measured at the inverter input terminal must be LESS THAN the maximum allowable input DC voltage of the inverter |  |  |  |  |  |
| No. | Description |  |  |  | Value | Accept | Reject | Reasons |
| 1 | Check whether the measured DC voltage falls within the allowable MPPT voltage range of the inverter. (Only for String Inverter ) |  |  |  |  |  |  |  |
| 2 | Check whether the measured Grid Phase Voltage are within the acceptable limit. (Single Phase - 243V max / 216V min) (Three Phase – 440V max / 376V min) |  |  |  |  |  |  |  |
|  | L1 to N |  |  |  |  |  |  |  |
|  | L2 to N |  |  |  |  |  |  |  |
|  | L3 to N |  |  |  |  |  |  |  |
| 3 | Check whether the measured Grid Line Voltage are within the acceptable limit. (Single Phase - 243V max / 216V min) (Three Phase – 440V max / 376V min) |  |  |  |  |  |  |  |
|  | L1 to l2 |  |  |  |  |  |  |  |
|  | L2 to L3 |  |  |  |  |  |  |  |
|  | L1 to L3 |  |  |  |  |  |  |  |
| 4 | Check whether the voltage of Phase to Earth are within the acceptable limit. (Single Phase - 216V to 253V) (Three Phase – 216V to 253V per phase) |  |  |  |  |  |  |  |
|  | L1 to E |  |  |  |  |  |  |  |
|  | L2 to E |  |  |  |  |  |  |  |
|  | L3 to E |  |  |  |  |  |  |  |
| 5 | Check whether the voltage of Neutral to Earth are within the acceptable limit. |  |  |  |  |  |  |  |
|  | Condition | Acceptable NEV |  |  |  |  |  |  |
|  | Normal Operation | < 3V |  |  |  |  |  |  |
|  | Best Practice range | 0.5V to 2V |  |  |  |  |  |  |
|  | Warning Threshold | > 3V - investigate |  |  |  |  |  |  |
|  | Critical concern | > 5V – unsafe, must be rectified |  |  |  |  |  |  |
| Photographs for each test ( 1 to 5) |  |  |  |  |  |  |  |  |

HSE MAXIS SITE PACK

GENERAL INFO

| Applicant Name (System Installer): |  |
| --- | --- |
| Site PIC Name (at site): IC/Passport No.: | Mobile No.: |
| Company Name (Main Vendor/Contractor): | Sub-Contractor/Vendor name: (if applicable) |
| Project: GCPV system installation | Work description: |
| LRD/Address: (ensure same with PART A site info) | Work Area/Room: Rooftop : Front porch : DB room : |
| Permit duration: Start date End date: |  |
| Request by (Maxis): | Mobile No: |

Emergency Contact Number:

| No | Description | Phone No. | Remark |
| --- | --- | --- | --- |
| 1 | Local Hospital |  |  |
| 2 | Nearest Clinic |  |  |
| 3 | Nearest BOMBA |  |  |
| 4 | Nearest Polis station |  |  |
| 5 | HSE/Safety Officer/Site Safety Supervisor |  |  |
| 6 | Main Office No. |  |  |

Worker name list.

| No | Name | Toolbox day 1 | Toolbox day 2 (if installation extended beyin 1 day)( |
| --- | --- | --- | --- |
| 1 |  |  |  |
| 2 |  |  |  |
| 3 |  |  |  |
| 4 |  |  |  |
| 5 |  |  |  |

Note:

1. Attached another name list if required

2. Valid CIDB, WAH, NTMSP or other relevant card/cert refer to next page

3. All incident (Accident & Near miss) to be report immediately at Maxis

Workers card photo: (CIDB, WAH, NTMSP)

| No | Name | CIDB | WAH | NTMSP | Valid Work Permit (foreign workers) | Signature |
| --- | --- | --- | --- | --- | --- | --- |
| 1. |  | Ref: Expiry date: Photo | Ref: Expiry date Photo | Ref: Expiry date Photo |  |  |
| 2. |  | Ref: Expiry date: Photo | Ref: Expiry date Photo | Ref: Expiry date Photo |  |  |
| 3. |  | Ref: Expiry date: Photo | Ref: Expiry date Photo | Ref: Expiry date Photo |  |  |
| 4. |  | Ref: Expiry date: Photo | Ref: Expiry date Photo | Ref: Expiry date Photo |  |  |
| 5. |  | Ref: Expiry date: Photo | Ref: Expiry date Photo | Ref: Expiry date Photo |  |  |

Maxis HSE Site Pack Photographs

- Site Toolbox Meeting & Safety Briefing

- PPE Compliance Photo

- Equipment Inspection

- Sky lift Photos

Note:

1. Reflective vests to be used at ground level works, night work. Reflective vest cannot be used during climbing/working at height

2. Key collection will use NCR

3. Physical Safety site pack required, If online document not available on site at all times.

Lifting Operation and Lifting Equipment

(For manual operation or using Crane)

| Person in charge name: | Mobile No.: |
| --- | --- |
| Lifting method: (refer to lifting procedure) |  |
| Lifting material description: (Install or remove) | Estimated weight: |
| Height: |  |

| No | Description (Lifting equipment) | Yes | No | Remark |
| --- | --- | --- | --- | --- |
|  | Pulley |  |  |  |
|  | Sling |  |  |  |
|  | Connector/Shackle |  |  |  |
|  | Hook |  |  | Safety ledge available/function |
|  | Rope/Cable |  |  |  |
|  | Hoist assistance (Descender/etc) |  |  |  |

N/A – not applicable

Crane/Skylift Inspection

Height:

| No | Description | Yes | No | Remark |
| --- | --- | --- | --- | --- |
|  | PMA No & validity |  |  | PMA No: Reg No: Expiry date: |
|  | Out rigger |  |  |  |
|  | Out rigger plate/ground stability |  |  |  |
|  | Hydraulic system |  |  |  |
|  | Work area protection |  |  | Cone, signage, light, blinker |
|  | Operator PPE’s |  |  |  |
|  | Skylift bucket |  |  | For skylift |

1. Detail inspection to be conducted by Crane/Skylift operator

2. Workers that require to exit the skylift bucket to another level and expose to fall more than 2 meter require to have valid working at height competency from approved training vendor)

Electrical

| No | Description | Yes | No | Remark |
| --- | --- | --- | --- | --- |
| 1. | ELCB/Circuit breaker |  |  |  |
| 2. | Competence person |  |  | Wireman/Chargeman |
| 3. | PPE |  |  | Electrical glove |
| 4. | LOTO |  |  |  |

Hotwork

| No | Description | Yes | No | Remark |
| --- | --- | --- | --- | --- |
| 1. | Fire blanket (if applicable) |  |  |  |
| 2. | Observer (fire watcher) |  |  |  |

Note: Portable fire extinguisher is mandatory at site

Inspection

| No | Description | Yes | No | Remark |
| --- | --- | --- | --- | --- |
| 1. | Portable fire extinguisher |  |  |  |
| 2. | First Aid box |  |  |  |
| 3. | Safety Signage |  |  |  |
| 4. | Barricade tape (if applicable) |  |  |  |
| 5. | Safety Cone/Safety Signboard |  |  |  |
| 6. | Ear Protection |  |  |  |
| 7. | Eye protection |  |  |  |
| 8. | Hand protection |  |  |  |
| 9. | Other machinery |  |  |  |
| 10. |  |  |  |  |

Toolbox

PIC/Trainer name:

|  | Toolbox content |  | Toolbox content |
| --- | --- | --- | --- |
|  | Electrical Safety |  | Lifting operation |
|  | Working at Height |  | Housekeeping |
|  | Manual handling |  |  |
|  | Fire Safety |  | Hazard |
|  | PPE usage |  | Emergency Response |
|  | Hand tools |  |  |
|  | Power tools |  |  |
|  | Chemical |  |  |

Note: Signed at Workers Name list after toolbox briefing

Job Hazard Analysis (JHA)

(HIRARC refer to Safety Manual)

| Required PPE |  |  |
| --- | --- | --- |
| Sequence of Basic Job Steps | Potential Hazards | Recommended Action or Procedure |

Acceptance and Verification

| Prepared by |  |  | Verified and Accepted by |  |  |
| --- | --- | --- | --- | --- | --- |
| Signature | : |  | Signature | : |  |
| Name | : |  | Name | : |  |
| Position | : |  | Position | : |  |
| Company | : |  | Company | : |  |
| Date | : |  | Date | : |  |