PART A: SITE ACCEPTANCE REPORT AND INSTALLATION CHECKLIST

1.0 SITE INFORMATION

| MHS No | {siteName} | System Size Installed | {systemSize} |
| --- | --- | --- | --- |
| Installation Start Date | {startDate} | Installation End Date | {endDate} |
| System Installer | Ai Solar Sdn Bhd |  |  |
| PIC Onsite | {picName} |  |  |
| Premise Address | {address} |  |  |

Note:

Please ensure that the information filled out is correct.

2.0 SYSTEM COMPONENTS INSTALLED

| Item | Description | Quantity/Length |
| --- | --- | --- |
| PV Solar Panels | Trina Solar TSM NEG19.20 620W - {serialNumbers} | {panelQty} Nos |
| Inverter | (Huawei sun2000-10K-MAP0) 1. {inverterSn} | 1 Nos |
| Mounting Structure | Aluminium Solar Mounting structure and accessories | 1 Set |
| DC cabling | Helukable 1500v 4sq.mm | 1 Roll |
| AC Cabling | DNF PVC insulated Cable 450/750v 6sq.mm | 1 Roll |
| Solar combiner box | IP65 14 Ways Combiner Box | 1 Nos |
| AC breakers | 4P C25 TAXNELE MCB | 1 Nos |
| AC SPD | 3 PHASE 40kA TYPE 2 SPD | 1 Nos |
| Wifi Dongle | SDongleA-05 SN: {dongleSn} | 1 Nos |
| Smart Meter | Acrel ADL 400 | 1 Nos |

3.0 DRAWINGS

- Single Line Diagram – (Kindly attach as per sample below)

{%img_sld}

- PV Layout submission to SEDA – (Kindly attach as per sample below)

{%img_pvlayout}

4.0 INSTALLATION PHOTOGRAPHS

Notes:

*Photos to be captured with GPS (latitude / longitude) information, time and date; shown on photo

*Please attach maximum 3 photographs per page, please ensure that photographs are of great viewing quality.

*Ideally please utilize full page per item.

* All photos must be labelled

- Solar Panel Array Layout

{%img_array}

- AC and DC Cable Route

- DC Route {%img_dc_route} - AC Route {%img_ac_route}

- Inverter or Microinverter

{%img_inverter}

- Combiner Box

{%img_combiner}

- Interconnection Point at the Customer’s Distribution Board (DB)

{%img_interconnection}

- Housekeeping at customer premise after installation completed.

{%img_housekeeping}

5.0 TESTING & COMISSIONING RESULTS

  - Cable Insulation Test (For String Inverter System)

| Cable Insulation Test |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Test Point |  | All cables |  |  |  |  |
| Use appropriate tools to measure and record |  |  |  |  |  |  |
| Testing is conducted on new cable installations to determine if the insulation has been damaged. Notes: Mandatory for all test on-site photographs to be attached and labelled accordingly. |  |  |  | Instructions: SWITCH OFF / DISCONNECT the following: - PV AC MCB Isolate all cables except for inter-module connection and earthing cables. |  |  |
| No. | Cable from (Originating) | Cable to (Terminating) | Insulation Resistance Value (M Ohms) |  | Pass | Fail |
|  |  |  |  |  | (Please tick the relevant box) |  |
| For String Inverter System |  |  |  |  |  |  |
| 1 | PV String 1 (+) | MPPT Inverter | >200 |  | / |  |
| 2 | PV String 1 (-) | MPPT Inverter | >200 |  | / |  |
| 3 | PV String 2 (+) | MPPT Inverter | >200 |  | / |  |
| 4 | PV String 2 (-) | MPPT Inverter | >200 |  | / |  |
| 5 | Inverter | AC MCB | >200 |  | / |  |
| 6 | AC MCB | PV Meter | >200 |  | / |  |
| 7 | AC MCB | AC SPD | >200 |  | / |  |
| 8 | PV Meter | Load Main Breaker | >200 |  | / |  |
| For Micro Inverter System |  |  |  |  |  |  |
| 1 | PV Panels | Microinverter 1 |  |  |  |  |
| 2 | PV Panels | Microinverter 2 |  |  |  |  |
| 3 | PV Panels | Microinverter 3 |  |  |  |  |
| 4 | PV Panels | Microinverter 4 |  |  |  |  |
| 5 | PV Panels | Microinverter 5 |  |  |  |  |
| 6 | PV Panels | Microinverter 6 |  |  |  |  |
| 7 | PV Panels | Microinverter 7 |  |  |  |  |
| 8 | Junction Box | AC MCB |  |  |  |  |
| 9 | AC MCB | ELCB |  |  |  |  |
| 10 | ELCB | PV Meter |  |  |  |  |
| 11 | AC MCB | AC SPD |  |  |  |  |
| 12k | PV Meter | Load Main Breaker |  |  |  |  |
| Photographs: |  |  |  |  |  |  |

  - String Open Circuit Voltage Test

| String Open Circuit Voltage Test |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Point |  | Solar Combiner Box |  |  |  |  |  |  |  |
| Use appropriate tools to measure and record |  |  |  |  |  |  |  |  |  |
| Test the continuity of each string |  |  |  |  |  | OK: |  | Not OK: |  |
| Determine the following: 1. Measured Open Circuit Voltage (Voc_mea) of each string. 2. Expected Open Circuit Voltage (Voc_exp) of each string. 3. % Difference between measured and expected Voc. ACCEPT if - % difference of Voc (between measured Voc and expected Voc) with respect to expected Voc is within +/- 5% - Voc measured of each string is less than the maximum input voltage of the inverter - Polarity of all DC cables (string and array) is correct Notes: Mandatory for all test on-site photographs to be attached and labelled accordingly. |  |  |  |  |  | Solar irradiance should be at least 350 Wm-2 when performing this test. Instructions: SWITCH OFF / DISCONNECT the following: - PV AC MCB |  |  |  |
| String No. | Voc of string at STC (V) |  | Voc measured (V) | Voc expected (V) | Measured module temp (oC) | Measured Irradiance (Wm-2) | % difference of Voc |  | Accept (A) or Reject (R) |
| 1 |  |  |  |  |  |  |  |  | A |
| 2 |  |  |  |  |  |  |  |  | A |
| 3 |  |  |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |  |  |
| Photographs: String 1: {%img_string1} String 2: {%img_string2} |  |  |  |  |  |  |  |  |  |

DC Short Circuit Current Test

| DC Short Circuit Current Test |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Test Point | Solar Combiner Box |  |  |  |  |  |  |
| Use appropriate tools to measure and record |  |  |  |  |  |  |  |
| Using appropriate method, determine the following: 1. Measured short circuit current (Isc_mea) of each string 2. Expected short circuit current (Isc_exp) of each string 3. % Difference between measured and expected Isc. ACCEPT if % difference of Isc (between measured Isc_mea and expected Isc_exp) with respect to Isc_exp is within +/- 5% Notes: Mandatory for all test on-site photographs to be attached and labelled accordingly. |  |  |  |  | Solar irradiance should be at least 350 Wm-2 when performing this test. Instructions: SWITCH OFF / DISCONNECT the following: - PV AC MCB |  |  |
| No. String No. | Solar irradiance (Wm-2) | Measured module temp (oC) | Measured Isc of string (A) | Expected Isc of String (A) |  | % difference of Isc | Accept (A) or Reject (R) |
| 1 |  |  |  |  |  |  | A |
| 2 |  |  |  |  |  |  | A |
| Photographs: |  |  |  |  |  |  |  |

  - Isolation Device Functional Test

| Isolation Device Functional Test |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Test Point |  | All breakers and switches |  |  |  |
| Use appropriate tools to measure and record |  |  |  |  |  |
| Please tick in the appropriate box Notes: Mandatory for all test on-site photographs to be attached and labelled accordingly |  | Solar irradiance should be at least 350 Wm-2 when performing this test. Instructions: SWITCH OFF / DISCONNECT the following: - PV AC MCB |  |  |  |
| No. | Description |  | Accept | Reject | Note |
| 1 | Confirm voltage is NOT present at the outgoing terminal of PV AC MCB when the switch is in OFF position |  |  |  |  |
| 2 | Confirm voltage is present at the outgoing terminal of PV AC MCB when the switch is in ON position |  |  |  |  |
| Photographs: |  |  |  |  |  |

  - Inverter Functional Test and Incoming power supply measurement.

| Inverter Functional Test |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Point |  |  |  | Inverter |  |  |  |  |
| Use appropriate tools to measure and record |  |  |  |  |  |  |  |  |
| Notes: Mandatory for all test on-site photographs to be attached and labelled accordingly |  |  | Please tick in the appropriate box Solar irradiance should be at least 350 Wm-2 when performing this test. Instructions: SWITCH ON the system and ensure that the inverter is operating. CAUTION: Before switching on the inverter, make sure Voc measured at the inverter input terminal must be LESS THAN the maximum allowable input DC voltage of the inverter |  |  |  |  |  |
| No. | Description |  |  |  | Value | Accept | Reject | Reasons |
| 1 | Check whether the measured DC voltage falls within the allowable MPPT voltage range of the inverter. |  |  |  |  |  |  |  |
| 2 | Check whether the measured Grid Phase Voltage are within the acceptable limit. (Single Phase - 253V max / 216V min) (Three Phase – 440V max / 376V min) |  |  |  |  |  |  |  |
|  | L to N |  |  |  | {1p_ltn} |  |  |  |
| 3 | Check whether the measured Grid Line Voltage are within the acceptable limit. (Single Phase - 243V max / 216V min) (Three Phase – 440V max / 376V min) |  |  |  |  |  |  |  |
|  | L to N |  |  |  | {1p_ltn} |  |  |  |
| 4 | Check whether the voltage of Phase to Earth are within the acceptable limit. (Single Phase - 216V to 253V) (Three Phase – 216V to 253V per phase) |  |  |  |  |  |  |  |
|  | L to E |  |  |  | {1p_lte} |  |  |  |
| 5 | Check whether the voltage of Neutral to Earth are within the acceptable limit. |  |  |  | {1p_nte} |  |  |  |
|  | Condition | Acceptable NEV |  |  |  |  |  |  |
|  | Normal Operation | < 3V |  |  |  |  |  |  |
|  | Best Practice range | 0.5V to 2V |  |  |  |  |  |  |
|  | Warning Threshold | > 3V - investigate |  |  |  |  |  |  |
|  | Critical concern | > 5V – unsafe, must be rectified |  |  |  |  |  |  |
| Photographs: L-N {%image_1p_ltn} L-E {%image_1p_lte} N-E {%image_1p_nte} |  |  |  |  |  |  |  |  |

PART B: HSSE MAXIS SITE PACK

GENERAL INFO

| Applicant Name (System Installer): {customer_name} |  |
| --- | --- |
| Supervisor/PIC Name (at site): {engineer_name} IC/Passport No.: {engineer_ic} | Mobile No.: {engineer_phone} |
| Company Name (Main Vendor/Contractor): Ai Solar Sdn Bhd | Sub-Contractor/Vendor name: (if applicable) |
| Project: Residential GCPV system installation | Work description: Solar Installation |
| LRD/Address: {address} | Work Area/Room: Rooftop : Front porch : DB room : |
| Permit duration: Start date: End date: |  |
| Request by (Maxis): | Mobile No: |

Emergency Contact Number:

| No | Description | Phone No. | Remark |
| --- | --- | --- | --- |
| 1 | Hospital: Damansara Specialist Hospital | 0377181000 |  |
| 2 | Nearest Clinic: Klinik Medilove Damansara Uptown | 01156568863 |  |
| 3 | Nearest BOMBA: Damansara Fire and Rescue Station | 0377294444 |  |
| 4 | Nearest Polis station: Damansara Police Station | 0377222222 |  |
| 5 | HSE/Safety Officer/Site Safety Supervisor |  |  |
| 6 | Main Office No. |  |  |

Worker name list.

| No | Name | Toolbox day 1 | Toolbox day 2 (if installation extended beyond 1 day) |
| --- | --- | --- | --- |
| 1 | MOHD HAYEE | / | / |
| 2 | OSMAIZA BIN OMAR | / | / |
| 3 | MUHAMMAD AN NUBLI BIN MOHD ROZI | / | / |
| 4 | MOHD DANIAL FAHMI BIN MOHD RASHIB | / | / |
| 5 | AFIK AFIAT BIN BUSRA | / | / |

Note:

1. Attached another name list if required

2. Valid CIDB, WAH, NTMSP or other relevant card/cert refer to next page

3. All incident (Accident & Near miss) to be report immediately at Maxis

Workers card photo: (CIDB, WAH, NTMSP)

| No | Name | CIDB | WAH | NTMSP | Valid Work Permit (foreign workers) |
| --- | --- | --- | --- | --- | --- |
| 1. | MOHD HAYEE | Ref:w91060120140024 Expiry date:10/26 | Ref: Expiry date Photo | Ref: Expiry date Photo |  |
| 2. | MUHAMMAD IZZAT HILMI BIN SAIMAN | Ref:001102140173 Expiry date: 21/11/2027 | Ref: 001102140173 Expiry date: | Ref: Expiry date Photo |  |
| 3. | OSMAIZA BIN OMAR | Ref: Expiry date: Photo | Ref: Expiry date Photo | Ref: Expiry date Photo |  |
| 4. | MUHAMMAD AN NUBLI BIN MOHD ROZI | Ref: Expiry date: Photo | Ref: Expiry date Photo | Ref: Expiry date Photo |  |
| 5. | MOHD DANIAL FAHMI BIN MOHD RASHIB | Ref: Expiry date: Photo | Ref: Expiry date Photo | Ref: Expiry date Photo |  |
| 7. | AFIK AFIAT BIN BUSRA | Ref: 920603146159 Expiry date: 03/06/2027 | Ref: Expiry date Photo | Ref: Expiry date Photo |  |

Maxis Site Pack Photographs

- Site Toolbox

{%img_toolbox}

- Safety Briefing & Toolbox Meeting (capturing tools, safety gear, and PPE compliance)

{%img_safety}

- Equipment Inspection

{%img_inspection}

- Sky lift Photos

{%img_skylift}

Note:

1. Reflective vests to be used at ground level works, night work. Reflective vest cannot be used during climbing/working at height

2. Key collection will use NCR

3. Physical site pack required, If online document not available

Lifting Operation and Lifting Equipment

(For manual operation or using Crane)

| Person in charge name: Lee Skylift Sdn Bhd | Mobile No.: |
| --- | --- |
| Lifting method: (refer to lifting procedure) |  |
| Lifting material description: Install | Estimated weight: LESS THAN 200KG |
| Height: |  |

| No | Description (Lifting equipment) | Yes | No | Remark |
| --- | --- | --- | --- | --- |
|  | Pulley |  | / |  |
|  | Sling |  | / |  |
|  | Connector/Shackle |  | / |  |
|  | Hook |  | / | Safety ledge available/function |
|  | Rope/Cable |  | / |  |
|  | Hoist assistance (Descender/etc) | / |  |  |

N/A – not applicable

Crane/Skylift Inspection

Height:

| No | Description | Yes | No | Remark |
| --- | --- | --- | --- | --- |
|  | PMA No & validity | / |  | PMA No: PMA-NS/A25-85583 Reg No: NS-PMA-114552 Expiry date:19/8/2026 |
|  | Out rigger | / |  |  |
|  | Out rigger plate/ground stability | / |  |  |
|  | Hydraulic system | / |  |  |
|  | Work area protection | / |  | Cone, signage, light, blinker |
|  | Operator PPE’s | / |  |  |
|  | Skylift bucket | / |  | For skylift |

1. Detail inspection to be conducted by Crane/Skylift operator

2. Workers that require to exit the skylift bucket to another level and expose to fall more than 2 meter require to have valid working at height competency from approved training vendor)

Electrical

| No | Description | Yes | No | Remark |
| --- | --- | --- | --- | --- |
| 1. | ELCB/Circuit breaker | / |  |  |
| 2. | Competence person | / |  | Wireman/Chargeman |
| 3. | PPE | / |  | Electrical glove |
| 4. | LOTO |  |  |  |

Hotwork

| No | Description | Yes | No | Remark |
| --- | --- | --- | --- | --- |
| 1. | Fire blanket (if applicable) |  | / |  |
| 2. | Observer (fire watcher) |  |  |  |

Note: Portable fire extinguisher is mandatory at site

Confined Space

| SECTION 1: Application (To be completed by Applicant) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Applicant Name |  | Company |  | Date |  |
| IC/Passport No. |  | Location |  | Start Time |  |
| Equipment No. |  | Work Order No |  | End Time |  |
| Work Description |  |  |  |  |  |

| SECTION 2: ISOLATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Piping/Ducting |  | Barricade |  | Other engulfment material |  |
|  | Mechanical/Electrical Room |  | Material/Sand/Soil |  | Others |  |
| The items ticked have been isolated or made safe. Verify by Entry Supervisor Name: Sign Date |  |  |  |  |  |  |

| SECTION 3: ATMOSPHERIC MONITORING (To be filled by Authorised Gas Tester: AGT) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Type of Gas | Acceptable Range | Test 1 | Test 2 | Test 3 | Test 4 | The conditions are safe for entry under the conditions ticked below |  |
| O2 | 19.5 – 23.5% |  |  |  |  |  |  |
| Flammable | <10% LEL |  |  |  |  |  |  |
| CH4 | < 25 ppm |  |  |  |  | With a supplied air respirator |  |
| H2S | < 10 ppm |  |  |  |  | With an air purifying respirator |  |
|  |  |  |  |  |  | Without a respiratory protective device |  |
| AGT Signature |  |  |  |  |  |  |  |
| AGT Name |  |  |  |  |  | Remarks: |  |
| Time |  |  |  |  |  |  |  |
| Instrument Serial No |  |  |  |  |  |  |  |
| Instrument Calibration Date |  |  |  |  |  |  |  |

| SECTION 4: STAND-BY PERSONNEL AND RESCUE ARRANGEMENTS (To be filled by Person Applicant) |  |  |
| --- | --- | --- |
| Stand-by personnel Name | 1. | Rescue facilities, equipment and communication with Entry Supervisor & Rescue Personnel |
|  | 2. |  |
|  | 3. |  |
|  | 4. |  |
| Verify by Entry Supervisor Name: Sign: |  |  |

SECTION 5: PERMIT AUTHORIZATION (To be filled by Permit Issuance)

Base on my evaluation, the confined space described above is in a safe condition for work to be done, provided that the precautions above are fully observed. Entry date: Entry Time: to Permit issuer Name: Signature

SECTION 6: PERMIT ACCEPTANCE (To be filled by Entry Supervisor)

I understand the procedures required for entry and work in the confined space and the protective measures and equipment to be used Entry Supervisor Name: Signature: Date:

SECTION 7: SIGNING OUT (to be filled by Entry Supervisor and Permit Issuer)

All persons & Equipment have been withdrawn and the work has been completed. Any further entry requires a new confined space permit to be applied Entry Supervisor Name Signature Date Permit Issuer Name Signature Date

SECTION 8: DEBRIEFING (to be conducted by Permit Applicant and Entry Supervisor with Work Party)

Debriefing note:

Inspection

| No | Description | Yes | No | Remark |
| --- | --- | --- | --- | --- |
| 1. | Portable fire extinguisher | / |  |  |
| 2. | First Aid box | / |  |  |
| 3. | Safety Signage |  | / |  |
| 4. | Barricade tape (if applicable) | / |  |  |
| 5. | Safety Cone/Safety Signboard | / |  |  |
| 6. | Ear Protection |  | / |  |
| 7. | Eye protection |  | / |  |
| 8. | Hand protection | / |  |  |
| 9. | Other machinery |  | / |  |
| 10. |  |  |  |  |

Toolbox

PIC/Trainer name:

|  | Toolbox content |  | Toolbox content |
| --- | --- | --- | --- |
|  | Electrical Safety |  | Lifting operation |
|  | Working at Height |  | Housekeeping |
|  | Manual handling |  |  |
|  | Fire Safety |  | Hazard |
|  | PPE usage |  | Emergency Response |
|  | Hand tools |  |  |
|  | Power tools |  |  |
|  | Chemical |  |  |

Note: Signed at Workers Name list after toolbox briefing

Job Hazard Analysis (JHA)

(HIRARC refer to Safety Manual)

| Required PPE |  |  |
| --- | --- | --- |
| Sequence of Basic Job Steps | Potential Hazards | Recommended Action or Procedure |
| Lifting Materials | Falling Object | Barricade area and signal man |
| Cable Termination to House DB | Electric shock | Insulation Rubber Glove and Shutdown power supply |
| Cutting Materials | Equipment Malfuction and impact on workers | Regular inspection, Proper PPE and follow SOP. |